Attachment A - Technical Specifications

Bid 26-115 Annual Supply of Fire Service Meters

Bidder Name:  ___________________________________________

Instructions:

Circle Yes or No under the Meets Specs.  If bidder circles No, explain how the quality to the desired meter is achieved in the Exceptions space.  Explain in detail the deviation from the ability to meet the specification, and an explanation of how this would be determined to be an acceptable alternative to meeting the condition.  Exceptions/Alternatives must be detailed in such a way that allows such deviations to be fully evaluated. The City shall determine at its sole discretion whether the bidder’s exception is an acceptable alternative.  Upload the completed form in the Response Attachments in Ebid.

| Meets Specs |  | Technical Specifications Fire Service Meters 6” – 12” |
| --- | --- | --- |
|  |  | - Performance and Standards |
| Yes | No | - Meters shall have the following operating performance requirements: Meter Size; Operating Range 98.5% - 101.5% Accuracy; Low Flow Registration @ % Accuracy; Max. Continuous Flow. 6-inch; 2.5 - 2500 gpm; 1.5 gpm @ 95% min.; 2000 gpm. 8-inch; 2.5 - 4500 gpm; 1.5 gpm @ 95% min.; 3500 gpm. 10-inch; 2.5 - 7000 gpm; 1.5 gpm @ 95% min.; 5500 gpm. 12-inch; 4 - 7000 gpm; 2.5gpm @ 95% min.; 5500 gpm. Exceptions: |
| Yes | No | - All meters shall comply with the latest revision of AWWA C703 for positive displacement type, magnetically driven, cold-water meter. Exceptions: |
| Yes | No | - Water Meters shall meet or exceed new meter accuracy standards set forth in the latest revision of AWWA Standard C703 for displacement type, magnetically driven, cold-water meter. Exceptions: |
| Yes | No | - All materials and components used in the manufacturer of the meters shall comply with all applicable AWWA standards and the Safe Drinking Water Act. Exceptions: |
| Yes | No | - Meters shall be constructed of “No Lead” brass alloy in compliance of Federal Public Law 11-380. Exceptions: |
| Yes | No | - Operating principal shall be low flows are measured by positive displacement, nutating disk design and high flows are measured by a turbine meter. Low and high flows are defined as below or above the specified crossover flow rate. Exceptions: |
| Yes | No | - Spring loaded cross over valve actuated without the use of weights. Exceptions: |
| Yes | No | - Meters shall be delivered with HRE registers wired for connection to Itron 100W+ pit style endpoints, capable of clip-on mounting to register. Note: CFG-0151-006 125-foot cable thin insulation (with protective cover) for factory potting directly to meter register by meter manufacturer. Exceptions: |
| Yes | No | - Test results and/or certification files of supplied meters shall be submitted by electronic mail. Exceptions |
| Yes | No | - All measuring elements of the meter including the registers cross over valve and turbine shall be field serviceable and replaceable without removal of the meter. Exceptions: |
|  |  | - Meters |
| Yes | No | - All meters shall be supplied with two (2) sets of bar-coded labels for scanning of the water meter serial number. Exceptions: |
| Yes | No | - One label shall be affixed to the case of the water meter, and the other included in the shipping container. Exceptions: |
| Yes | No | - Label shall clearly show meter test results for low, medium and high flow rates. Exceptions: |
| Yes | No | - All meters shall be supplied with one (1) bar coded test result label affixed to meter body showing low, medium and high flow test results in % of actual flow rate. Exceptions: |
| Yes | No | - Serial number shall be stamped on each casing. Exceptions: |
| Yes | No | - Water meter shall be marked as “No Lead”, “NL” or other proprietary marking to indicated compliance with Federal Public Law 11-380 Exceptions: |
| Yes | No | - Water meter case shall be marked with raised characters denoting meter size, meter, model and direction of water flow. Exceptions: |
| Yes | No | - Meters shall be capable of a maximum operating pressure of 175 psi without damage or leakage. Exceptions: |
| Yes | No | - Metering chamber shall be constructed of corrosion resistant polymer material. Exceptions: |
| Yes | No | - All other metallic meter components shall be stainless steel. Exceptions: |
| Yes | No | - Flanged inlet and outlets, Class 150 Exceptions: |
|  |  | - Strainer |
| Yes | No | - Strainer shall have an effective straining area of at least six (6) times the open area of the inlet pipe. Exceptions: |
| Yes | No | - Maximum head loss across the strainer shall be 4 psi at the safe maximum rated capacity Exceptions: |
| Yes | No | - Strainers body shall be ductile iron or epoxy-coated steel with removable lid to provide easy access for cleaning or service Exceptions: |
| Yes | No | - Strainer screen or basket shall be stainless steel. Exceptions: |
|  |  | - Low Flow and High Flow Registers |
| Yes | No | - High Resolution Encoder (HR-E) register with 8 register dials, providing minimum measurement resolution of: - 0.1 cubic feet for meter sizes less or equal to 2” - 1 cubic foot for meters sizes 6” thru 10” - 10 cubic feet for meter sizes greater than or equal to 12” Exceptions: |
| Yes | No | - Straight reading. Exceptions: |
| Yes | No | - Permanently sealed and waterproof. Exceptions: |
| Yes | No | - Magnetic driven. Exceptions: |
| Yes | No | - Bayonet type mounting and removable without disruption to water meter. Exceptions: |
| Yes | No | - Unit of measure and visual register reading in cubic feet. Exceptions: |
| Yes | No | - Read wheels with minimum 5/32” high font for numerals with white read wheels for 100 cubic feet increments and larger, and black read wheels for ten (10) cubic feet increments and smaller. Exceptions: |
| Yes | No | - Low flow registration shall have 8 moving dials with a registration capacity of 9,999,999.9 cubic feet. Exceptions: |
| Yes | No | - a.) High flow registration shall have a total of 8 moving dials with a registration capacity of 99,999,999 cubic feet (6”-10”) - b.) High flow registration shall have a total of 8 moving dials with a registration capacity of 999,999,990 cubic feet (12”) Exceptions: |
| Yes | No | - 360° test circle with ten major divisions and ten minor divisions per major division. Exceptions: |
| Yes | No | - Leak detector dial. Exceptions: |
| Yes | No | - Tamper resistant set screw for mounting. Exceptions: |
| Yes | No | - Sealed and moisture proof circuitry. Exceptions: |
| Yes | No | - Register factory mounted using tamper resistant seal screw unless specified by City. Exceptions: |
| Yes | No | - Registers shall have a serial number under the lid and not match the serial number of the meter body. (Registers can have a serial number under the register lid that matches, but is not required to match, the serial number of the meter body. If the register serial number is printed on the outside of the register lid, it must not match the meter body serial number.) Exceptions: |
| Yes | No | - Each meter supplied under these specifications must be tested for registration accuracy at flow rate and test flow quantities in accordance with AWWA C703. Exceptions: |
| Yes | No | - The Manufacturer must furnish a certificate showing that each meter has been tested for accuracy of registration and that it complies with accuracy and capacity requirements of AWWA C703 when tested in accordance with AWWA Manual, M6. Exceptions: |
|  |  | - Warranties |
| Yes | No | - Meter housings shall be warranted to retain structural integrity for a minimum period of 18 months. Exceptions: |
| Yes | No | - Meter registers shall be warranted to function for a minimum period of 25 years for disc meters, and 5 years for turbine meters, following shipment. Exceptions: |
| Yes | No | - Meters shall be warranted to retain AWWA C703 new meter reading accuracies in accordance with manufacturer’s normal and customary warranty period. Please provide details below or in the Response Attachments tab in Ebid. Warranty Details: |