INVITATION TO BID – Annual District Fire Alarm & Sprinkler Testing and Inspection Services

BID #WCSD6-27-699-0618

Weld County School District 6

Scott Francies, Purchasing Manager

Weld County School District 6

1025 9th Ave

Greeley, CO. 80631

Ph:  970-348-6151 | Fax:  970-348-6033

Email: sfrancies@greeleyschools.org

Your bid is requested for “Annual District Fire Alarm & Sprinkler Testing and Inspection” per the attached specifications.  Questions regarding this bid may be directed to Scott Francies at 970-348-6151.

The necessary documents are available online at the Rocky Mountain E-Purchasing System site (Bidnet). Go to http://www.RockyMountainBidSystem.com, then “Bid Opportunities” and then select “Weld County School District 6”.

Interested respondents are requested to submit bids prior to 2pm, Wednesday, July 1, 2026 to the email listed above. Only electronic replies will be accepted. Sfrancies@greeleyschools.org

Weld County School District Six reserves the right to reject any or all bids for good cause as deemed to be in the best interest of School District Six.

Weld County School District Six encourages and participates in cooperative purchasing endeavors undertaken by or on behalf of other governmental jurisdictions.  To the extent, other governmental jurisdictions are legally able to participate in cooperative purchasing endeavors; the District supports such cooperative activities.  Further, it is a specific requirement of this proposal or Request for Proposals that pricing offered herein to Weld County School District Six may be offered by the vendor to any other governmental jurisdiction purchasing the same products.  The vendor(s) must deal directly with any governmental agency concerning the placement of purchase orders, contractual disputes, invoicing, and payment.  Weld County School District Six shall not be liable for any costs or damages incurred by any other entity.

Be advised that price will not be the only criteria of award; vendor performance and service history with School District Six will also be considered.

Thank you for submitting a competitive bid to Weld County School District Six.

Sincerely,

Scott Francies

Purchasing Manager

Weld County School District Six

BID #WCSD6-27-699-0618

SCOPE:

Weld County School District 6 ("District") is seeking proposals from qualified, licensed fire protection contractors to provide comprehensive, combined inspection, testing, and maintenance (ITM) services for both fire alarm systems and fire sprinkler systems across various District facilities.

The objective is to establish a long-term agreement with a single vendor to ensure 100% compliance with National Fire Protection Association (NFPA) standards, including NFPA 25 (sprinkler systems), NFPA 72 (fire alarm systems), and all applicable local fire codes.

Contract Term: The District intends to enter into a contract for an initial term, with options for annual renewals, to secure multi-year compliance and consistent service continuity.

PROJECT MANAGER:

Michael Scholfield

Network and Infrastructure Manager

970-348-6501

Mscholfield@greeleyschools.org

REQUESTED ITEM(S):

Annual Performance Based Testing/Inspection of Fire Alarm System(s) and Sprinkler Systems:

Please see attached list of location and quantity

The selected vendor shall provide all labor, materials, equipment, and expertise required to perform the following services

Section A: Fire Alarm Testing & Inspection Services

Annual performance-based testing and inspection must include, but is not limited to:

 System Integrity & Environment: Inspect all fire alarm control panels, remote panels, and peripheral equipment to verify they are in service, operating satisfactorily, and free of detrimental site conditions. Inquire regarding modifications to systems, building occupancy, or general storage environments.

 Initiating & Notification Devices: Test all smoke and heat detectors in accordance with manufacturer specifications. Inspect and test all annunciators and zones visually and by tripping a detector.

 Detector Maintenance & Sensitivity: Clean 100% of all detectors per manufacturer guidelines. Conduct an annual sensitivity test on 50% of detectors per year, providing a certification report.

 Testing Restrictions: No smoke detection testing shall be performed using magnet testing, open flames, or acrid smoke.

 Electrical & System Components: Inspect and meter all batteries, inspect output relays, and test their activation. Test non-restorable heat detector circuits by simulating electrical operation. Function-test all accessible heat-actuating devices electrically and pneumatically.

 Interconnected Systems: During testing, activate outputs to verify equipment shutdown, start-up, and proper HVAC/smoke control functionality. Inspect and exercise flow switches, tamper switches, and low-pressure alarms.

 Maintenance & Programming: Tag devices as required. Include fire panel maintenance and device programming at no additional charge for up to six (6) times a year.

#### Section B: Fire Sprinkler Inspection, Testing, & Maintenance (ITM)

Annual, semi-annual, and quarterly ITM services must include, but are not limited to:

 Visual & Operational Tests: Conduct visual inspections and operational testing of all wet and dry pipe systems, including risers, gauges, and valves. Conduct main drain tests, water flow alarm tests, and supervisory signal testing (tamper switches).

 Dry Systems: Perform annual trip testing of dry valves and clean all strainers/filters.

 Fire Pump Testing: Conduct annual performance flow tests per NFPA 20 where applicable at specific sites.

 Obstruction Investigation: Inspect sprinkler heads for adequate clearance and verify they are completely free of paint, corrosion, or physical obstructions.

#### Section C: Documentation & Reporting

- Reporting: Compile a complete, typewritten report for each facility within ten (10) business days of testing. Reports must outline the general state of the systems, clearly highlight any deficiencies or "red-tagged" items, and recommend corrective actions in accordance with recognized care and maintenance codes.

- Familiarization: Familiarize designated District agency personnel with the proper operation of the equipment

### Contractor Requirements

 Licensing & Qualifications: The contractor must be a licensed Fire Sprinkler and Fire Alarm Contractor in the State of Colorado.

 Personnel: All technicians servicing District fire alarm and fire sprinkler systems must hold NICET certifications or equivalent, recognized industry qualifications relevant to their discipline.

 Emergency Response: The contractor must provide 24-hour availability for emergency repairs with a maximum three (3) hour onsite response time.

 Equipment: The contractor must utilize their own calibrated gauges, meters, and testing equipment.

 Testing Window: All testing and maintenance work must be closely coordinated with the Facilities Department to minimize disruptions to school operations. Summer execution or after-hours testing may be required.

### Proposal Submission Requirements

 Company Profile: Documented years in business and specific technical experience working with educational facilities or governmental agencies.

 Staffing Plan: A comprehensive list of lead technicians dedicated to this project, including copies of their relevant certifications.

 References: A minimum of three (3) references from government or school district clients for whom similar combined services have been rendered.

 Insurance Verification: Proof of statutory insurance coverage, including General Liability ($1,000,000), Workers' Compensation, and Automobile Liability.

Responses to this RFP shall be sent to Scott Francies via e-mail at sfrancies@greeleyschools.org.  RFP responses must be received by 2:00 PM MST, Wednesday, July 1, 2026 to be considered valid.

FIRE ALARM INSPECTIONS $_______________________________________

SPRINKLER TESTING $____________________________________________

TOTAL BID PRICE $_______________________________________

Will Vendor accept Visa as Payment?		YES_____	NO______

By submitting a bid for Bid #26-791-417, you acknowledge that you understand and comply with all conditions and terms governed by this bid. You understand and acknowledge that bids shall become the exclusive property of Weld County School District Six upon receipt and shall be subject to public inspection and copying in accordance with the Colorado Open Records Act, C.R.S. §§ 24-72-200.1 et seq. In issuing this RFP, the district is not seeking, and advises bidders not to submit, trade secrets or confidential commercial or financial information. The district shall have no obligation to withhold all or any part of a proposal in response to an open records request. You further certify that this bid is made without prior understanding, agreement or connection with any business or person submitting a competitive bid and without prior commitment or influence from any person or department from Weld County School District Six for this same material or service: and therefore, is in all respects fair and without collusion or fraud.  Collusive bidding is a violation of State and Federal law and can result in fines, imprisonment, and civil damages.  Bids received without this signed statement will be handled as non-responsive.

Further, by submitting a bid for Bid #WCSD6-26-791-1216, you acknowledge and certify that if your product or service is “information and communication technology” (ICT) as defined by the Colorado Office of Information Technology, your product or service complies with all applicable provisions of §§24-85-101, et seq., C.R.S., and the Accessibility Standards for Individuals with a Disability, as established by the Office of Information Technology pursuant to Section §24-85-103(2.5). Any additional costs to add accessibility features will be the obligation of the bidder, and any addition or change to the price proposal will be disallowed.

Payment will be made to the vendor submitting pricing for this bid unless otherwise noted.  It is the responsibility of the vendor to inform School District Six of this information prior to a purchase order being processed.  If this information is not made available to Weld County School District Six prior to this time, it is the responsibility of the vendor submitting this bid to issue payment to another party.

VENDOR NAME___________________________________________________________________

AUTHORIZED SIGNATURE__________________________________________________________

PRINT AUTHORIZED SIGNATURE____________________________________________________

PHONE NUMBER__________________________     FAX NUMBER__________________________

EMAIL ADDRESS _________________________________________________________________

DATE__________________________________