## ATTACHMENT #1
Network Infrastructure Construction Material | [6 empty] | Task#: S3O-25-005~014H, AIE-A1 (AIE-Area1)
NO | Item | P/N | MANUFACTURE | DESCRIPTION | QTY | UNIT | U/PRICE | AMOUNT
1 | Fiber Optic Cable, SM-72C | LT-DJBGEBA1-72 | LS | Single Mode 72 Core ITU657A1 Fiber Optic Cable Cable Description: Attenuation 0.22dB @1550nm per kilometer, Max 0.2 ps/√km (20 section link) PMD, Attenuation vs. Bending (10mm radius x 1turn) max 0.75 dB @ 1550 nm, Loose tube, Dry cored, PE insulated fiber core, all dielectric single HDPE jacket non-amor, max. 20D Mandrel diameter, 6 Fiber per Bundle, comply ITU-T G.652 and suitable underground conduit use. OR Equivalent. 900Mx1RL: The SM72-core fiber optic cable shall be provided as one continuous 900-meter roll. | 900 | MT
2 | Fiber Optic Cable, SM-12C | LT-DJBGEBA1-12 | LS | Single Mode 12 Core ITU657A1 Fiber Optic Cable Cable Description: Attenuation 0.22dB @1550nm per kilometer, Max 0.2 ps/√km (20 section link) PMD, Attenuation vs. Bending (10mm radius x 1turn) max 0.75 dB @ 1550 nm, Loose tube, Dry cored, PE insulated fiber core, all dielectric single HDPE jacket non-amor, max. 20D Mandrel diameter, 6 Fiber per Bundle, comply ITU-T G.652 and suitable underground conduit use. OR Equivalent. 2,600Mx1RL: The SM12-core fiber optic cable shall be provided as one continuous 2,600-meter roll. | 2600 | MT
3 | Fiber Distribution Patch Panel (Rack Type) - 4U | CCH-04U | Corning | Corning Cable System CCH-04U Closet Connector Housings - Holds 12 CCH Connector Panels Included CCH Connector Panel (CCH-CP12-59) 6 Duplex SC(12Core)-12ea with Blank Module - 12ea Included Cable Trays. OR Equivalent | 1 | SET
4 | Fiber Distribution Patch Panel (Rack Type) - 1U | CCH-01U | Corning | Corning CCH-01U Closet Connector Patch Panel Housings - Holds 2 CCH Connector Panels, Included CCH Connector Panel (CCH-CP12-59) 6 Duplex SC(12Core)-2ea with Blank Module - 2ea, Included Cable Tray. OR Equivalent. | 9 | SET
5 | Fiber Distribution Patch Panel (Wall Type), SM-12C | WCH-02P | Corning | Holds up to 2 CCH connector panels Included Cable Tray. Locking Availability-Provider door and jumper door are lockable. Dimensions (H x W x D)-18.8 cm x 42.2 cm x 10.7 cm (7.4 in x 16.1 in x 4.2 in) Wall-Mountable Connector Housing (WCH) OR Equivalent. | 4 | SET
6 | Fiber Optic Splice Closure, 72 Core for Duct | STC-HTM-KT3-72 | SUNIL | FO Splice Manhole Closure (for 48 Cores) - In-line type closure - Either single-loose fibers or ribbon fibers are available - Either heat-shrink sleeves or mechanical splice sleeves are available - Robust mechanism for clamping the cable sheath - Accept additional cables without removal of the sheath retention or disturbing existing splices - Do not require special tool or equipment for installation. OR Equivalent. | 1 | EA
7 | SM-12 Core SC Pigtail | Pigtail, SM-12C (SC type) |  | SM-12 Core SC Pigtail , Fanout Cord-6.6ft. | 30 | EA
8 | 10U Wall Mount Rack Cabinet | DAW-10U | Dong A Worid | Wall type Rack with fan, Ground Bus Bar, Rack Mount Power Panel(110V). (Approximate size: W 600 mm x D 600 mm x H 600 mm ) OR Equivalent. | 6 | EA
9 | Pull Box |  |  | Fiber optic cable Pull Box, Wall mount, (Demension: about (W) 400 mm x (H) 400 mm x (D) 200 mm), Waterproof Box. | 8 | EA
10 | MaxCell Fabric Innerduct with 3cells | 6428-3 | Milliken | MaxCell Fabric Innerduct with 3cells - Fabric breaking tensile > 41.8 kg/cm - Low coefficient of friction – Dynamic COF of 0.12 on HDPE - Pull tapes pre-installed in each cell (225 kg, 565 kg, 815 kg, 1,135 kg, or MaxGlide) - Product pre-lubricated to further lower tension during cable pulls - Life span of approximately 30 years - Not affected by climate & Temperature range is – 30 ℃ to 100℃ - UL 2024A LSZH Plenum Rating FR versions for inside plant usage - Max. cable OD 28mm and Width 64mm, 3 Cells type - Orange Color and OptiCell OR Equivalent. 1,500Mx1RL: Maxcell fabric innerduct to be supplied as one continuous 1,500-meter roll. | 1500 | MT
Total