###### STATEMENT OF OBJECTIVES

GENERAL

Contractor shall quote and provide all labor, travel, expenses, parts, materials, tools, equipment, supervision, and expertise necessary to provide a functional standalone IP Address network based, wired Public Address (PA) System for the

Fargo VA Medical Center

2101 N. Elm St.

Fargo, ND 58102

The new PA headend equipment will be placed next to the current location(2C25) and will work in conjunction with the current system until it is fully installed, tested and operational. This is to allow for maximum continuous coverage.  The new system will work with the existing speakers, nurse call/code blue, lynx system and phone system. The system shall be a fully redundant Network in case a network switch would fail.

CONFORMANCE STANDARDS

Contract service shall ensure that the equipment functions in conformance with the latest published edition of applicable industry standards, including but not limited to the National Electric Code (NEC), National Fire Protection Association (NFPA-99), National Fire Protection Association (NFPA-72), National Fire Protection Association (NFPA-70),   Underwriters Laboratories (UL), Occupational Safety and Health Administration (OSHA), Veterans Affairs (VA), Center for Devices and Radiological Health (CDRH), Federal, State, and local codes. Within the Veteran Affairs regulations, particular focus on conformance with relevant documents SECTION 27 51 16: PUBLIC ADDRESS AND MASS NOTIFICATION SYSTEMS, SECTION 27 52 23: NURSE CALL AND CODE BLUE SYSTEMS, and SECTION 26 20 00 INTERIOR DISTRIBUTION SYSTEM. Equipment defined herein shall be maintained in accordance with the manufacturer's standards/specifications.

OBJECTIVES

The US Department of Veterans Affairs (VA) is seeking a contractor to provide, install, and maintain a functional wired Public Address System for the Veterans Affairs Medical Center to provide the best safety and care for our Veterans during their stay. The Public Address system will provide enhanced ability to provide alerts and information throughout the facility in a clear and targeted manner via the use of PA zoning capabilities. Per the VA Telecommunications and Special Telecommunications Systems Design Manual, the PA System has been identified as an emergency communications system and performs the Primary Facility NFPA Life Safety Code Blue Team Notification. PA System Head End equipment will be in existing closets. The PA System will be operated in accordance with VA standards.

Contractor shall not add or substitute any component(s) without prior approval from the CO (Contractor Officer). The contractor shall be fully licensed to perform the work. The Contractor shall deinstall and remove the current systems. A formal on-site survey shall be conducted to finalize system requirements prior to beginning any installation activities.

  - The contractor shall provide a comprehensive turnkey solution that enables the Fargo VA to provide a public address system that is accessible hospital wide, to all areas, buildings, and floors identified by the VA.

SYSTEM DESCRIPTION

Design Requirements

Provide a Public Address System, capable of distributing the indicated audio signals from equipment including LAN controllers, communication links, cabling, (minimum 1 hour) battery backup, power line surge protection and all other necessary components to make a complete and operational system. Complete coverage will be provided for identified main interior campus buildings and outbuildings.

Provide a zoned system capable of evenly distributing live, and pre-recorded paging and music program sources.  Provide balanced and highly intelligible distributed sound free of noise and distortion.  Provide capability of both individual and simultaneous paging all separate paging zones.  Intelligibility must meet the requirements of Modified Rhyme Test (MRT) of ASA S3.2. The system will have volume control by zone.

Provide all headend interface, amplification components, conditioners, and any other equipment necessary.  Provide system capable of interfacing with the telephone system for zone paging. This project will and connect the Overhead paging into the existing LYNX system per code.

Provide all materials and labor needed for a refresh of all Headend and subcomponents for a complete and operational system for the services in this specification plus the additional system capabilities as indicated. This includes but not limited to all necessary equipment, interfaces, jumpers, terminations, cabling, amplifiers, conditioners, power supplies, battery backup, software and all components required for system operation.

SYSTEM PERFORMANCE

The system shall provide even sound distribution throughout the designated

area, plus or minus 3 dB for the 1/1 octave band centered at 4000 Hz.  The

system shall provide uniform frequency response throughout the designated area, plus or minus 3 dB as measured with 1/3-octave bands of pink noise at locations across the designated area selected by the Contracting Officer Representative (COR) or POC (Point of Contact).  The system shall be capable of delivering 75 dB average program level with additional 10 dB peaking margin sound pressure level (SPL) in the area at an acoustic distortion level below 5 percent total harmonic distortion (THD).  Unless otherwise specified the sound pressure reference level is 20 micro-Pascal (0.00002 Newtons per square meter).

Necessary System Capabilities

- Must be a standalone IP address networked system.

- Must be wired.

- RMF Accredited

- Provide a public address system with capabilities to support zone paging, background music, all-call, priority paging, pre-automated outputs, messaging processors, software, input modules, controllers, and interface modules.

- Paging priorities will be provided upon design/implementation in accordance with clinical input.

- Must be capable of interfacing with all components of the Fire Safety system

- Capable of interfacing with the new Nurse Call system

- Provide power supplies that provide sufficient power for worst-case conditions of system operation that could occur without signal loss or perceptible degradation.

- Provide power line surge protection for all equipment connected to AC power. Provide surge protection integral to the equipment or installed as an accessory item in accordance with manufacturer's recommendations. Do not use fuses for surge protection.

- Electrical Requirements:105 VAC to 130 VAC at 60 Hz operating voltage range, plus or minus 2 percent

- System shall have warning capabilities for critical issues, such as system failure, to decrease or eliminate asset loss

- Zoning Capabilities throughout facility to ensure targeted messaging

- Must adhere to requirements of SECTION 27 51 16: PUBLIC ADDRESS AND MASS NOTIFICATION SYSTEMS

- Install wiring in rigid steel conduit, intermediate metal conduit, cable trays, or electric metallic tubing as specified in Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.

- Install conduit if necessary or required

- All grounding practices shall comply with NFPA 70

- Must provide on-site user training for staff

- Comply with all VA security and information security requirements.

- VAMC needs a system that has a simple/basic user interface that can be used by someone with little knowledge of the system

- 24/7/365 phone support

- Install shall be completed to ensure minimal impact on the business operations of the facility. Installation shall be phased during normal hours of coverage, as well as after-hours as needed to minimize patient risk, disruption, and maintain facility operations.

- System is capable of the addition of future applications and the expansion to additional areas (e.g., additional devices and rooms, zones, floors, new buildings, etc.).

- Operating systems shall remain current with OEM (e.g., Microsoft, etc.) support life cycle and patching

- Must be capable of providing public address access twenty-four (24) hours per day, three-hundred and sixty-five (365) days per year

- Biomedical Engineering must be able to dictate the programming and responsiveness of the system in each area

- Biomedical Engineering must be able to adjust zoning setups as needed or requested by Hospital Leadership

- Biomedical Engineering must be able to customize and configure outgoing address settings by severity as needed in the system

- After installation, Contractor must provide as built schematics

- System must be designed for hospital use

- System must be a complete and fully operational system at the conclusion of the hardware and software installation

- Monitoring capability to alert Biomedical Engineer, and AOD (Administrator on Duty) to errors/failures, so they may respond accordingly

- Must be capable of expanding to future areas and receive notifications in those respective areas

- Must install a system that is a supported Windows OS (Windows 11 and above, and Server 2019 and above).

- All Windows, Cisco and all required Network and operational Licenses will be supported by a minimum of one (1) year from Go Live. Go Live is determined by final payment depending upon the Government’s inspection and acceptance of the work performed

- Existing system must be active until the new system passes testing and installation is complete for Go-live

- New equipment racks and switches will be added as necessary to support the new IP equipment

- Racks shall be lockable.

- The new PA System will utilize zoning to allow isolated communication to the specific areas as necessary or to allow campus wide messaging when desired

- The system will have volume control by zone

- The Contractor shall replace existing touchscreen panels

- For equipment: Date of manufacture must not be greater than 2 years before the purchase order date

SCOPE OF WORK

The Contractor shall quote, design, and provide a fully turn-key operational Public Address System.  The Contractor shall manage the project in its entirety. The Contractor shall deinstall and remove the current systems. All equipment becomes the property of the VA after installation and acceptance. A single contractor shall perform all tasks directly related to design, procurement, installation, and implementation. The Contractor shall provide System Utilization Reports, management, and maintenance of the wired and wireless access points, and the network required to support any wired and wireless access points.

Work shall include designing and providing a refresh of the public address system as required and as described for the Fargo VAMC. The Contractor shall provide a turnkey system capable of receiving, processing, and transmitting indicated input signals including the system wiring, raceways, pull boxes, terminal cabinets, outlet and mounting boxes, control equipment, amplifiers, microphones, wired speakers, mounting hardware and other accessories and miscellaneous items required for a complete operating system even though each item is not specifically mentioned or described.

The contractor shall provide a system complete and ready for operation. The Contractor shall maintain a Help Desk through phone support (24x7) for User Support. Support includes monitoring, calibration, and maintenance of the installed wired and wireless networks and the performance of those networks at the medical center. The installed system shall perform according to the technical specifications and procedures provided for within this SOW. The help desk maintenance, support, and managed services include all hardware, software, and infrastructure.

Contractor shall provide documentation of the network and include updated maps/drawing (as built) showing installed components.

TESTING REQUIREMENTS

Operational Test: Perform tests that include originating program and page messages at microphone outlets, preamplifier program inputs, and other inputs. Verify proper routing and volume levels and that system is free of noise and distortion.

Signal-to-Noise Ratio Test: Measure signal-to-noise ratio of complete system at normal gain settings as follows:

- Disconnect microphone at connector or jack closest to it and replace it in the circuit with a signal generator using a 1000-Hz signal. Replace all other microphones at corresponding connectors with dummy loads, each equal in impedance to microphone it replaces. Measure signal-to-noise ratio.

- Repeat test for each separately controlled zone of loud wired speakers.

- Minimum acceptance ratio is 50 dB

Distortion Test: Measure distortion at normal gain settings and rated power. Feed signals at frequencies of 50, 200, 400, 1000, 3000, 8000, and 12,000 Hz into each preamplifier channel. For each frequency, measure distortion in the paging and all-call amplifier outputs. Maximum acceptable distortion at any frequency is 3 percent total harmonics.

Acoustic Coverage Test: Feed pink noise into system using octaves centered at 500 and 4000 Hz. Use sound-level meter with octave-band filters to measure level at five locations in each zone. For spaces with seated audiences, maximum permissible variation in level is plus or minus 2 dB. In addition, the levels between locations in same zone and between locations in adjacent zones must not vary more than plus or minus 3 dB.

Power Output Test: Measure electrical power output of each power amplifier at normal gain settings of 50, 1000, and 12,000 Hz. Maximum variation in power output at these frequencies must not exceed plus or minus 1 dB.

Public address system will be considered defective if it does not pass any of the required individual tests and inspections listed above. Results must be administered to COR.

SITE VISIT

It is strongly suggested and expected that the offeror inspect the campus to be serviced to fully understand the nature of the work and the conditions under which the work is to be performed. In no case shall failure to inspect the campus constitute grounds for a claim after contract award.

CONTRACTING OFFICER AUTHORITY:

The Contracting Officer is the only person authorized to approve changes or modify any of the requirements under this contract. The Contractor shall communicate with the Contracting Officer on all matters pertaining to contract administration.  Only the Contracting Officer is authorized to make commitment or issue changes that will affect price, quantity or quality of performance of this contract.  In the event the Contractor effects any such change at the direction of any person other than the Contracting Officer, the change shall be considered to have been made without authority, and no adjustment will be made in the contract price to cover any increase in cost incurred thereof.

- Contractor to reuse parts of existing infrastructure to include but not limited to the following equipment (racks, ups units, PA speakers, cabling and fiber optic cabling.)

- Contractor to identify and label all equipment and provide detailed system design drawing(s).

- Contractor to provide all spec sheets and manuals of installed equipment.

- All access to equipment room locations to be coordinated with POC.

###### HOURS OF WORK

Work shall be scheduled for a Monday-Friday schedule 7:30 am-4:30 pm time frame but if different times are needed this can be discussed and mutually agreed upon. Work will be scheduled in such a manner as to minimize disruption to facility services within the VA Healthcare campus.

Federal and National Holidays observed by the VAMC Include:

New Year’s Day 					Labor Day

Martin Luther King Jr. Day 				Columbus Day

President’s Day 					Veterans Day

Memorial Day 						Thanksgiving Day

Independence Day

Juneteenth

Also included would be any other day specifically declared by the President of the United States to be a National Holiday.

When a holiday falls on a Sunday, the following Monday shall be observed as a legal holiday by U.S. Government agencies. When a holiday falls on a Saturday, the preceding Friday shall be observed as a legal holiday.

INSPECTION AND ACCEPTANCE

The Contractor shall conduct a joint inspection with the COR once all equipment has been delivered and installed. The COR shall inspect all phases of delivery and installation and provide a punch list of any issues.

The Contractor will work with Supply Chain to ensure equipment is properly labeled before installation.

The COR shall ensure all work is completed satisfactorily prior to acceptance.  Disputes shall be resolved by the Contracting Officer.

Re-Performance of Non-Conforming Work. Upon inspection of work, any work found to not be in accordance with this PWS/contract shall be re-performed by the contractor at no additional cost to the government.

Installation shall be phased during normal hours of coverage, as well as after-hours as needed to minimize patient risk, disruption, and maintain facility operations.  Any after-hours shall be approved by the PO prior to any work performed.

Contractor shall be responsible for all equipment until installed and accepted by the Government. All required equipment shall be fully installed by the Contractor.

The Contractor shall be responsible for storing all equipment and supplies until the time of the installation. Off-site storage for all equipment and supplies until day of installation.

The VA facility will not accept and store equipment until the time of the installation.

The Contractor shall remove all related shipping debris and cleanup; any construction associated with delivery and installation of the specified items. Contractor shall remove all packaging from the Fargo VA premises. The Contractor shall be responsible for any damage to any building that occurs due to Contractor error or neglect.

The contractor shall coordinate all deliveries, staging areas, installations, and parking arrangements with the COR. Upon coordination with COR for installation, the contractor shall inform the Contracting Officer of any problems which may be anticipated about installation, or which will affect optimum performance once installation is completed.

DELIVERY AND INSTALLATION

The vendor will be responsible for delivering and installing a fully accepted project within 180 days ARO.

All items to be shipped F.O.B. destination. Shipping shall be included in the product 	price and shall not be billed separately.