I.	GENERAL

- Scope of Work

Contractor to furnish all material, tools, labor, equipment and transportation necessary to clean and sanitize complete fans and air-conditioning duct systems.  Work is to include supply fans, hot and cold deck plenums, all related duct work, and all vent fan units, including kitchen exhaust hoods, all building exhaust fans and office fan coil units.

- Location & Time

The project is located at Porterville Developmental Center, 2650l Avenue 140, Porterville, CA 93257, specifically, Unit W1, E2, and Pharmacy and tied-in areas. This project is time constricted and contractor shall perform this work as directed by the Chief of Plant Operations III, or his designee.

- Reference Codes and Standards

The reference documents below (latest edition unless otherwise indicated), form a part of these specifications and are located in the Plant Operations Office for referral.

California Code of Regulations

California Building Standards Code

- Required Submittals

All information listed below shall be submitted in triplicate to the Chief of Plant Operations III or his designee within 10 calendar days of the award of the contract. No work shall begin prior to the submission/approval of this information.

a.    In order to verify equipment contractor shall submit vacuum specifications

(manufacturer, model number and minimum CFM).

b.	Identification and listing of all products and sources.

c.  	Certificate of Compliance for all materials used on this contract.

d. 	Manufacturer's samples, specifications and written Material Safety Data Sheets for each product.

e. 	System manufacturer's certification that the contractor has the training and qualifications to install the manufacturer's product.

f.	Schedule of how the contractor proposes to accomplish the work and progress dates.

- EQUIPMENT SPECIFICATIONS

Contractor must provide power vacuum equipment, which draws a minimum of 9000 CFM and provides 4 to 5 inches W.F. of vacuum at the plenum.

- CONTRACTOR'S QUALIFICATIONS

The contractor shall meet the requirements or be certified by the National Air Duct Cleaners Association (NADCA). The contractor shall perform source removal duct cleaning and clean to the NADCA cleaning standard. Contractor shall show proof of compliance with specifications of a similar nature within the last twelve months. Projects completed must be of similar size and complexity as this project. The contractor shall submit a client reference for at least three commercial or industrial HVAC systems rehabilitation and cleaning projects of similar type, size, and degree of difficulty completed within the last two years. Copies of NADCA certificate or, proof of compliance, and client references shall be submitted with the bid.

- PROJECT REPORTING

Prior to the commencement of the project, the contractor shall take photographs/video of the internal parts of the fan system ducts at points specified by the Chief of Plant Operations III, or his designee. After cleaning, the contractor shall take additional photographs/video at these specified points and any other location requested by the Chief of Plant Operations III, or his designee (minimum of thirty [30] total photographs per fan, plus video of random ducts).  Contractor to supply four (4) random videos; two (2) on the supply and two (2) on the return, as designated by the Chief of Plant Operations III, or his designee.

a.	Pressure readings of the system and across the coils shall also be taken before and after the cleaning to ensure proper cleaning. Reading shall be taken under a full load condition.

b.	Motor Amperage readings shall be taken before and after the fan cleaning.  Readings shall be taken under full load conditions.

c.	Air samples shall be taken from each air handling system. At least three (3) samples from the supply side down stream of the cooling coils, before the air filters, and three (3) from the return side after the air filters. These samples shall be sent to an independent laboratory for analysis and tested for microbiological growth. The samples shall be taken using the Anderson Impactor method.

d.	Final approval will be given by the Chief of Plant Operations III, or his designee, after all specifications have been met and a project report containing all the above elements have been submitted to, and approved by the Chief of Plant Operations III.  All cleaning shall be verified in accordance with the National Air Duct Cleaners Association standard's test for cleanliness.

- SCHEDULE OF WORK

All work shall be performed in accordance with time provisions agreed upon by the contractor and the Chief of Plant Operations III, or his designee.  Contractor shall work premium time to the extent specified in the agreement, or as required to complete the work on schedule.

- TRAVEL

No mileage, travel time, or fuel costs shall be charged for traveling from portal to portal.

- MAINTAINING EXISTING SERVICES

The heating and ventilation system shall be shut down for work between the hours of 7:00 a.m. to 4:30 p.m., and returned to service before leaving the facility each day. Any deviation from the schedule shall be approved by the Chief of Plant Operations III, or his designee.

- PROPER EQUIPMENT

The contractor shall provide all staging, scaffold, ladders, or similar equipment to properly carry on the work, unless agreed with Porterville Developmental Center. Contractor shall furnish his own paint booth, which shall comply with all existing county air quality standards and regulations. Contractor shall obtain prior approval of Chief of Plant Operations III, or designee, for designated paint booth location.

- CLOSING UP OF UNINSPECTED WORK (IF REQUIRED)

The contractor shall not allow or cause any of the work to be covered up or enclosed until it has been inspected and approved by the Chief of Plant Operations III, or his designee.  Should any of his work be covered up or enclosed before such inspection, the contractor shall, at his own expense, uncover the work, and after it has been inspected and approved, make all repairs with such materials as may be necessary to make good.

- DAMAGE BY DIRT OR DUST

The contractor shall utilize caution to prevent spreading contamination to other areas. The contractor shall maintain negative air pressure while cleaning the fan system. Contractor will provide power vacuum equipment which draws a minimum of 9000 CFM and provides 4 to 5 inches W.G. of vacuum at the plenum.  All dirt and contamination dislodged during the cleaning process shall then be collected by the vacuum machine, thereby protecting the occupied space. Where small portable vacuum devices are used inside the building, filtration with 99.97% collection efficiency for capturing particles of 0.3 micron in size and larger shall be used. If the equipment has wheels or casters, they should be of a non-marking variety.

a.	The contractor shall be required to certify filter effectiveness of 99.97% efficiency of test results, from an independent testing agency for any filtration device when exhausting inside the building.

b.	All vacuums used for dry vacuuming during the cleaning process shall be HEPA type.

c.	The contractor shall seal the supply plenum opening with plastic sheeting as needed to insure contaminated air does not return to the building occupants.

d.	The contractor shall be responsible for insuring that all adjacent areas to the work are protected from water run off or seepage resulting from the cleaning process.

e.	The contractor shall insure the fan system is clean and ready for operation at the end of each day. The contractor shall notify Porterville Developmental Center's representative to inspect the fan system before they leave the job site. The contractor shall correct any deficiencies noted by the Porterville Developmental Center's representative at that time.

f.	The contractor shall be responsible for all damage to any equipment on the Porterville Developmental Center's premises, or machinery due to dirt, dust, or water attributed to the negligence of his work. The contractor shall clean, repair, or replace such damage at no expense to Porterville Developmental Center.

g.	All cleaning and sanitizing compounds used in the cleaning process must be E.P.A. registered for use in HVAC air distribution systems. The sanitizing solution shall be oxine or equivalent.

- ACCESS OPENING AND DOORS

All ductwork has been previously accessed. Existing ceiling access panels and ductwork sheet metal panels shall be utilized for proper cleaning. Original or new sheet metal panels with proper caulking and of the same or heavier gauge metal shall be used for repair/sealing of ducting after the cleaning process.

- CAULKING

Caulking shall be performed in a neat and effective manner. No caulking shall be applied over surfaces which would affect adhesion. All caulking shall be Locktite Super Flex Caulking Compound, or equal, as approved by Porterville Developmental Center.

- COILS (HEATING AND COOLING)

Coils and drain pans will be cleaned with coil clean concentrated coil cleaner. Drain lines are to be thoroughly cleaned and cleared before any pressure washing is performed, thus assuring complete and safe drainage.

- PLENUM AREAS

All interior walls, ceiling, and floors shall be vacuumed. Plenum areas shall be inspected and sealed air tight with an approved caulking compound.

a.	Fiberglass insulating material found to be in need of repair will be repaired or replaced and properly bonded with adhesive, clips, and proper lagging material.

b.	Fiberglass material shall be sealed with an approved encapsulant, after it has been thoroughly hand vacuumed.

- FANS AND FAN HOUSING

Fans and fan assemblies shall be thoroughly cleaned by use of vacuuming, use of cleansing water solution, and high pressurized washing. Degreasing, scraping, and wire brushing will be performed where required.

- FILTERS

New filters shall be installed when the unit has been completely cleaned. Filters shall be provided by PDC.

- DAMPERS

Duct mounted volume, fire and zone damper sets are to be marked at their current setting, then inspected and cleaned.

a.	All related equipment will be power vacuumed and high pressure washed where required. Areas with rust or scale build up will be wire brushed or scraped, and painted.

b.	All dampers, motors, and linkage will be lubricated and set into their original position upon completion of work in the plenum areas.

- Contractor shall paint only removable volume dampers that pull out, and not those that are stationary and sealed.

- AIR DUCTS (SUPPLY, RETURN, AND EXHAUST)

All ducts shall be thoroughly cleaned by vacuuming, brushing, air sweeping, and air whipping. Duct work that does not allow complete access shall be entered by means of access through supply, exhaust, and return air vents whenever possible. It is the expressed intent of this project to NOT penetrate or otherwise disturb ceilings/walls/etc. Any duct access requiring entry through a ceiling will be repaired in a professional and workmanlike manner, using the same materials and construction as the original ceiling, and ONLY with the written permission of the CPO lll. Access hatches may be substituted where applicable, again ONLY with the written permission of the CPO lll. Any damaged ducting or similar equipment noted during cleaning and requiring repair will be brought to the attention of the CPO lll, Porterville Developmental Center.

a.	Minor maintenance (i.e., caulking, sealing, reconnecting) of duct work will be performed in the normal course of the contractor's work.

- FIBERGLASS INSULATION MATERIAL

Fiberglass insulation material to be repaired will be of equal quality and thickness as contained in equipment requiring repair.

a.	Fiberglass will be sealed together by means of wall tacks, lagging tape, lagging adhesive, and lagging coating. Material used will be of the highest quality coating.

- SANITIZING

Sanitizing the air distribution network shall be performed as required using an EPA registered sanitizer. Prior approval by the Chief of Plant Operations III or designee is mandatory before using any sanitizer that would necessitate evacuation of clients.

a.	All registers are to be removed, numbered by location, and placed immediately into plastic bags. The sealed bag shall be taken to a predetermined site for cleaning, sanitizing, and painting.

b.	The registers will then be reinstalled upon completion of the cleaning of register boxes, and diffusers shall be set to their original position.

- SAFETY

The contractor shall supply Porterville Developmental Center with a copy of their code of safe practices and/or their written safety procedures, with their bid. The safety procedures must meet or exceed the requirements of the California State License Board.

a.	The contractor must obtain the proper clearances at the start of each work day from the control room.

b.	The contractor shall verify with Porterville Developmental Center's representative that the fan system to be worked on has been properly locked out and tagged out.

c.	Precautions shall be exercised when cleaning around electric motors, conduits, and electric fixtures to prevent electrical hazard and damage to equipment. The items shall be covered with plastic sheeting as required to prevent contact with water.

- FAN SYSTEM CLEANING

a.	All interior walls, ceilings, and floors shall be thoroughly cleaned by sweeping and vacuuming. All surfaces shall be scrubbed and sanitized with an approved solution.

b.	Coils and drain pans shall be cleaned with concentrated coil cleaner or equivalent, applied under pressure of not less than 200 PSI. Contractor shall follow this application with a fresh water rinse. The cleaning shall be done from the back of the coil to the front and continued until the coil is clean. All rust and foreign material shall be scrapped and wire brushed. Drain lines are to be thoroughly cleaned and cleared before any pressure washing is performed, thus assuring complete and safe drainage.

c.	Fan and housing shall be steam cleaned, degreased, and sanitized.

d.	Filter frames shall be washed and sanitized. New sealing tape shall be installed. Contractor shall remove and dispose of existing high efficiency filters. Contractor shall haul away and dispose of the filters, at the contractor's expense. Clean filters supplied by Porterville Developmental Center, shall be installed by the contractor.

e.	Outside air dampers shall be steam cleaned and sanitized. The contractor shall lubricate the dampers and linkages upon completion of the cleaning.

- FIBERGLASS INSULATION

- The contractor shall either replace or restore any loose or damaged insulation. Fiberglass insulation to be replaced shall be of equal thickness and quality as contained in the equipment requiring repair. The decision to restore damage rather than replace will be made by the Chief of Plant Operations III, or his authorized representative.

b.	All insulation shall be painted with a minimum of two coats of Fosters anti-fungicidal

40-20 coating, or equal, within the air handler room.

- DRAIN PANS

Pans shall be coated with Fosters anti-fungicidal drain pan coating, or state approved equal, with a minimum of three coats. Rusted coil supports shall be repaired with Devcon steel putty, or state approved equal. Rusted supports shall be prepared and coated with rustoleum primer and paint. All surfaces must be thoroughly dried before coating. Application must be scheduled to allow a minimum of six (6) hours drying time before fan operation is required.

- DOOR GASKETS

Door gaskets shall be inspected and replaced where needed to insure an effective leak free seal.

- ROOF-TOP VENTILATORS

The unit housing the fan blades shall be cleaned and inspected as per section 20.c above.       Electrical systems must be maintained to buildings.  Disconnected units must be reconnected and verification made for proper installation and operation.